## Sheet1
SPREADSHEET FOR CALCULATION OF GROUND-WATER PRODUCTION COSTS IN LOCAL CURRENCY AND METRIC UNITS
Dr. William M. Turner
http://www.agwconsultants.com
Email: senatorbil@aol.com
Tel: 011-505-843-7643
Fax: 011-505-246-2232
SEE NOTES AT END OF TABLE
Hydraulic Conductivity | m/d | 20 | 40 | 30 | 40 | 50 | 60 | 70 | 80 | WELL FUNCTION COEFFICIENTS
Aquifer Transmissivity | m2/d | 1000 | 2000 | 1500 | 2000 | 2500 | 3000 | 3500 | 4000 | a0 | -0.57722
Final Aquifer Transmissivity | m2/d | 6066.098 | 13491.1234 | 9751.1234 | 13491.1234 | 17231.1234 | 20971.1234 | 24711.1234 | 28451.1234 | a1 | 0.99999
Storage Coefficient | fraction | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | a2 | -0.24991
Static Water Level | m | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | a3 | 0.0552
Well Diameter | cm | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | a4 | -0.00976
Length of Original Water Column | m | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | a5 | 0.0010786
Length of Final Water Column | m | 40.5488 | 45.0907 | 43.4542 | 45.0907 | 46.0725 | 46.7271 | 47.1947 | 47.5453
Drawdown | m | 9.4512 | 4.9093 | 6.5458 | 4.9093 | 3.9275 | 3.2729 | 2.8053 | 2.4547
Total Lift | m | 59.4512 | 54.9093 | 56.5458 | 54.9093 | 53.9275 | 53.2729 | 52.8053 | 52.4547
Pumping Period | yrs | bar: 20 to 80
Design Continuous Pumping Rate | m3/d | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000
Total Annual Water Requirement | m3/yr | 5000000 | 5000000 | 5000000 | 5000000 | 5000000 | 5000000 | 5000000 | 5000000
Continuous Pumping Rate | m3/min | 5.5556 | 5.5556 | 5.5556 | 5.5556 | 5.5556 | 5.5556 | 5.5556 | 5.5556
Continuous Pumping Rate | l/s | 0.33327 | 0.33327 | 0.33327 | 0.33327 | 0.33327 | 0.33327 | 0.33327 | 0.33327
Electric Power Cost | Local/kWh | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Diesel Fuel Cost | Local/USgal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gasoline Fuel Cost | Local/USgal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Overall Pump Efficiency | fraction | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
Motor Efficiency | fraction | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
Pump Horsepower | BHP | 103.4002 | 95.5007 | 98.3469 | 95.5007 | 93.793 | 92.6546 | 91.8414 | 91.2315
Well Operating Factor | fraction | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6
Interest Rate | % | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
Period of Amortization | yrs | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
u | none | 2.0045e-07 | 2.0045e-07 | 2.0045e-07 | 2.0045e-07 | 2.0045e-07 | 2.0045e-07 | 2.0045e-07 | 2.0045e-07
Wu | none | 14.8455 | 15.4227 | 15.4227 | 15.4227 | 15.4227 | 15.4227 | 15.4227 | 15.4227
Drawdown | m | 9.4512 | 4.9093 | 6.5458 | 4.9093 | 3.9275 | 3.2729 | 2.8053 | 2.4547
Hourly Pumping Cost Per Well | Local | 11.0195 | 10.1777 | 10.481 | 10.1777 | 9.9957 | 9.8743 | 9.7877 | 9.7227
Minimum Annual Pumping Cost Per Well | Local | 96530.8474 | 89156.2211 | 91813.3208 | 89156.2211 | 87561.9613 | 86499.1214 | 85739.9501 | 85170.5716
Minimum Annual Total Pumping Cost | Local | 160884.7457 | 148593.7019 | 153022.2014 | 148593.7019 | 145936.6021 | 144165.2023 | 142899.9168 | 141950.9526
Well Cost Per Meter | Local | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
Minimum New Well Cost | Local | 16000 | 1171748.989 | 1194331.9853 | 1171748.989 | 1158199.1912 | 1149165.9927 | 1142713.708 | 1137874.4945
Wells Required Because of Excessive Drawdown |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wells Required to Meet Demand |  | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667
Number of Required Wells |  | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667
Annual Amortization Cost | Local | 6666.6667 | 488228.7454 | 497638.3272 | 488228.7454 | 482582.9963 | 478819.1636 | 476130.7117 | 474114.3727
Annual Maintenance Cost Multiplier | fraction | 2.22 | 2.22 | 2.22 | 2.22 | 2.22 | 2.22 | 2.22 | 2.22
Annual Maintenance Cost | Local | 357164.1354 | 329878.0181 | 339709.287 | 329878.0181 | 323979.2568 | 320046.7492 | 317237.8152 | 315131.1148
(Land, Buildings, Insurance, Salaries, Benefits,
Overhead, Vehicles, etc.)
Annual Operation & Amortization | Local | 524715.5477 | 478471.72 | 492731.4884 | 478471.72 | 469915.8589 | 464211.9515 | 460137.732 | 457082.0673
1. Except for aquifer transmissivity enter data in Column E only for items in boldface type. All other cells are calculated.
2. Values for aquifer transmissivity may be entered in any cell in Row 10.
3. If local currency is used, results will be in local currency.
4. Maintenance costs have been entered based on power costs. Experience from the City of Tucson indicates a multiplier of 2.22
You may change this multiplier by changing the formula in Cell (E53).
5. The Well Operating Factor is the proportion of time a well normally operates. Includes off peak and maintenance down time.
6. If you have suggestions for changes to this spreadsheet, please email us at: senatorbil@aol.com.